July 25, 2017

Mandy Kang

City of Manteca, Planning

1001 W Center St

Manteca, CA 95337

209.456.8518

SUBJECT: CENTERPOINT BUILDING COMPLETE LETTER: SPC-17-40

Dear Mandy:

CenterPoint has received City of Manteca comment letter on our trailer yard submission, we have excerpted your original letter and provided our responses below in red.  Separately, we have updated our exhibits, site plans, and preliminary design to incorporate the City’s notes.

Planning Division:

Comments:

- The address you have listed for this site is showing up as another property in our system and the APN for this site is showing up as 198-030-33. Is this site in the process of getting a new address? Are you completing a Lot Line Adjustment or Parcel Map to separate the parcels?

Applicant will propose to separate the individual parcels through LLAs once the current final map is approved and recorded.

- What will be the exact use for the site? Will the trucks/trailer positions be parked there indefinitely or will it be a truck terminal where they are constantly accessed? Will it be used for additional trailer/container parking for other adjacent sites? Do you need to add some vehicle parking stalls for the employees that may be taking the trucks to and from the sites?

Proposed uses will be surface storage of containers, chassis, and trucks; the sites will be developed / constructed in a manner to facilitate future development of a facility.  Currently we do not anticipate construction of a truck termination of trans load facility.  It is possible we will construct a small permanent office, or install a temporary office with a future Tenant Improvement request that will include parking.  We anticipate that prospective tenants will fall into the following categories: 1) an tenant with a facility in the area which will utilize the site for overflow storage and storage of materials within containers that are not high through put, 2) a tenant focused on intermodal use which will utilize the site to store containers, chassis, and trucks intended to distribute or on-load good utilizing the intermodal, and 3) a standard truck terminal operation, where long haul truck drop off containers at the yard which are then transferred to a short-haul truck for distribution closer to the population center (note we do not expect a full trans load operation which would include a trans load facility and significantly higher traffic counts).  We anticipate that all the prospective uses will require a Tenant Improvement modification subject to compliancy review by the City’s planning department, and drawings to be approved by the City’s building/engineering department, likely Tenant Improvements could include, signage, automatic gates, installation of auto parking stalls, installation of a temporary office structure (trailer), and installation of a freestanding office.

- Please provide an analysis that shows that this project is in compliance with the approved NWAWMP Environmental Impact Report. The light industrial sites were typically allowed for uses involving heavy trucks, automobile-services, mini-storage, various agricultural industries, industrial manufacturing or assembly uses, industrial storage, and truck and motor freight uses. In each case, the truck trips would have been limited.

The applicant has provided a detailed traffic analysis report showing that the proposed use follows the approved NWAWMP Environmental Impact Report.  We performed counts on the most conservative of the three potential use options (truck terminal operation) and verified based on physical counts that the proposed generate traffic similar to those as currently approved within the EIR.  We have also provided signal analysis in the area to show no deterioration of the level of service.  Additionally we have provided a detailed analysis of the current intersection in comparison with future intersection of the area to show that our proposed path of travel does not affect traffic flow on Airport Way.

Conditions of Approval {not all-inclusive):

- The previous Environment al Impact Report for the Northwest Airport Way Master Plan (SCH#2010022024) shall apply to this project. The end user shall comply with the users proposed in the EIR or additional environmental work shall be required for this project.

Agreed, applicant believes that the proposed use complies with the current zoning under the truck/motor freight uses.

- Project shall comply with all conditions and requirements of the approved Northwest Airport Way Master Plan for the CenterPoint Development.

Agreed, applicant expects to complete all adjacent infrastructure and frontage improvements are part of this project.

- All signage shall be submitted as a separate building permit from the building and shall comply with the Northwest Airport Way Master Plan and Chapter 17.54 of the Zoning Ordinance.

Agreed

- Street trees shall be provided along all public streets with a minimum of one tree installed for each thirty feet of frontage. One dominant tree, one alternate and two accent trees shall also be chosen for each street frontage from the City of Manteca approved Street Tree list.

Agreed, applicant has provided a NWAWMP compliant preliminary landscaping plan as part of its submittal package.

- The minimum planting size for trees shall be 15 gallon, with 25 percent of all trees on a project site planted at a minimum 24-inch box size. For commercial, office, community/civic, and industrial development, tree spacing within perimeter planters along streets and abutting residential property shall be planted no farther apart on center than the mature diameter of the proposed species.

Agreed, applicant has provided a NWAWMP compliant preliminary landscaping plan as part of its submittal package.

- No planter shall be smaller than 5 feet wide by 5 feet long, or 25 square feet, excluding curbing. Each planter shall include an irrigation system.

Agreed, applicant has provided a NWAWMP compliant preliminary landscaping plan as part of its submittal package.

- Required planting areas shall be permanently maintained by water, clearing debris and litter, weeding, pruning, insect control and replacement of plant materials and irrigation equipment as needed to preserve the health and appearance of plant materials. All trees, shrubs, and plants that, due to accident, damage disease or other cause shall be replaced.

Agreed, applicant has provided a NWAWMP compliant preliminary landscaping plan as part of its submittal package.

- Lighting:

  - Parking lots, driveways, trash enclosures/areas, public phones and group mailboxes shall be illuminated with a minimum maintained 1 foot-candle of light and an average not to exceed 4 foot-candles of light. The illumination shall not exceed 1O foot-candles in any one location.

Agreed, applicant has submitted a compliant updated lighting plan. See revised photometric plan.

Engineering Division:

General

- Comparison to the NWAWMP

  - The current parking lot configuration does not accommodate the layout of Road "I".

  - The 12" water line is to be installed in the full access road.

  - Backbone of the storm drain plan does not match the Master Plan. The documentation preciously sent to me regarding the modified storm drain plan did not include this section of the Master Plan. A Master Plan amendment will be required for approval of the modified plan.

The NWAWMP calls for the location of the road serving this southern parcel to be finalized with site plan approval; applicant is proposing to keep the road adjacent to Crothall as a full intersection.  As part of our proposal Applicant has provided a traffic analysis showing the proposes configuration to be compliant with the master plan and that it will not interfere with future development down the line, and applicant has also provide preliminary engineering design for the intersection to show its final configuration.

Site

- Show truck turn templates.

Depicted in civil and architecture plans

Transportation

The NWAWMP calls for the location of the road serving this southern parcel to be finalized with site plan approval; applicant is proposing to keep the road adjacent to Crothall as a full intersection.  As part of our proposal Applicant has provided a traffic analysis showing the proposes configuration to be compliant with the master plan and that it will not interfere with future development down the line, and applicant has also provide preliminary engineering design for the intersection to show its final configuration.

- Consolidate traffic on Street A to one lane at lntermodal Way intersection, same as Tactical Way/lntermodal Way.

- Correct CENTERPOINT WAY street label to INTERMODAL WAY. Water

- Bollards or some other protection device will be required around the hydrants in the trailer parking area.

- Ensure the locations of the future connection are located in a way that will allow meters and backflows to be installed immediately adjacent to roadway.

- If the 12" line is installed in Street A, the conditions will require it to be dedicated to the City for maintenance since there are services coming off of it; however, this line is not PFIP reimbursable.

Storm Drain

- Provide additional calculations showing the amount of bio retention needed vs. what is shown on the site plan and outlines of the DMAs.

Revised provided on plan

- What/where, is the pretreatment for the bio retention facilities?

Illustrated on the site plan and civil plan. See preliminary project storm water plan.

# Parks & Recreation

- A Community Facilities District (CFD), or other funding mechanism, shall be formed or annexed into, at the Developer's Expense for any landscape in City ROW, for areas between curb and sidewalk and the median on Airport, prior to City Council Acceptance of project improvements. CFD, or other funding mechanism fees shall be paid to the City by the Developer prior to Landscape Improvement Plans being signed and approved by the Parks & Recreation Department. Depending on timing of project will determine if a CFD formation or Annexation into existing CFD will be required.

Agreed

- All onsite improvements shall be maintained by the property owner.

Agreed

# Fire Department

- Site Address: Address numbers shall be plainly visible from the street fronting the property. Said address numbers shall contrast with their background and be a minimum of 12" in height

Agreed

- Fire Department Access:

  - Provide a diagram showing a minimum of 44' external radius and internal radius of 25' on all main entries, drive aisle and parking lot areas. The main drive aisle shall be designated Emergency Vehicle Access Lane and be a minimum of 26' wide.

  - A diagram showing proposed "Fire Lane" shall be submitted for approval to the Office of the Fire Marshal. Fire Lanes shall be marked in accordance with California Fire Code (Appendix D103.6 SIGNS and Manteca Fire Code 15.24

Agreed, fire access depicted per separate exhibit

- Fire Hydrants: Plans and specifications for fire hydrant systems shall be submitted for review and approval prior to construction.

  - Fire hydrants shall be installed on a minimum 8-inch looped water main.

  - Fire hydrants shall be installed around all buildings at a maximum spacing of 300 feet in accordance with the City of Manteca Standards and California Fire Code. Corners should be utilized for hydrant locations when possible.

  - Hydrants subject to vehicular damage shall be protected in an approved manner and not be obstructed by vehicles or other obstructions.

  - Provide 15 feet of clearance on either side of fire hydrant from stopped or parked vehicles.

Agreed, as depicted on civil drawings and per separate fire exhibit

- Underground piping for the fire sprinkler shall be approved by the Fire Department prior to permit issuance.

Agreed

- All above ground gas meter, regulators, and piping exposed to vehicular damage shall be protected in an approved manner.

Agreed

- Inspections. Fire protection systems (fire hydrants, water mains, etc.) shall be installed, tested and approved by the City prior to the issuance of any building permits. The Fire Department shall witness all system and acceptance tests. Please provide 24-hour notice prior to any system or acceptance tests. 209-456-8340

Agreed

- A Fire Department approved "key lock box" shall be properly installed near the main entrance. A 3200 series lock box can be order online directly from KNOXBOX.COM. Contact the Office of the Fire Marshal at FireMarshal@mantecafire.org for additional information.

Agreed

- All above ground gas meters, regulator, sand piping exposed to vehicular damage shall be protected in an approved manner.

Agreed

Please contact me if you have questions or concerns. I can be reached at (213) 488-8695 or wlu@centerpoint.com.

Sincerely,

William Lu

Senior Vice President, Development

CenterPoint Properties

Cc:

Attach: Letter from the Manteca Unified School District Letter from the San Joaquin Council of Governments Letter from SJCOG, Inc.

Letter from the South San Joaquin Irrigation District Letter from the Environmental Health Department